## Slide 1
i
Backup Relay C
Backup
Relay D
*
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
First Period (static) : t [0, Tqkh]
Line k Fault h
Second Period (transient): t [Tqkh, Tikh or Tjkh]
Line k Fault h
*
Iqkh ∢ qqkh
Ipkh ∢ qpkh
Iqkh /Pq
Ipkh / Pp
Ijkh ∢ qjkh
Iikh ∢ qikh
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh /Pj
I’ikh /Pi
Ijkh /Pj
Iikh /Pi
When a fault occurs at line k, location h pair relay performance (full, partial and no detection) can be enclosed
In one of the following six types:
Type 1: Complete fault detection in a relay pair q-p (case 1).
Type 2: Complete fault detection in a relay pair i-j (case 2).
Type 3: Partial fault detection in relay j in period 1.
Type 3a: Relay j is stuck due to loss sensitivity in period 1 (case 3)
Type 3b: Relay j is stuck due to current in the opposite direction in period 1 (case 4)
Type 3c: Relay j is stuck due to current in the opposite direction and no sensitivity in period 1 (case 5)
Type 4: Partial fault detection in relay i: Relay i is stuck due to no sensitivity in period 1 (case 6)
Type 5: Partial fault detection in relay i and relay j:
Type 5a: Relay i and j are stuck due to no sensitivity in period 1 (case 7)
Type 5b: Relay i is stuck due to no sensitivity and relay j is stuck due to current in the opposite direction in period 1 (case 8)
Type 5c: Relay i and j are stuck due to no sensitivity and relay j is stuck due to current in the opposite direction in period 1 (case 9)
Type 6: No fault detection at all
Type 6a: Relay p is stuck due to current in the opposite direction in period 1 (case 10)
Type 6b: Relay j is stuck due to current in the opposite direction in period 2 (case 11)
Type 6c: Relay p is stuck due to no sensitivity in period 1 (case 12)
Type 6d: Relay p is stuck due to current in the opposite direction and no sensitivity in period 1 (case 13)
Type 6e: Relay i is stuck due to current in the opposite direction in period 2 (case 14)
Type 6f: Relay j is stuck due to no sensitivity in period 2 (case 15)

## Slide 2
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 1: Complete fault detection in a relay pair q-p (case 1).
This happens when fault urrents at q and p go in the same direction at first period, and
Relays p and q are both sensitive at first period
Iqkh ∢ qqkh
Ipkh ∢ qpkh
Iqkh >Pq
Ipkh >Pp

## Slide 3
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 2: Complete fault detection in a relay pair i-j (case 2).
This happens when fault currents at i and j go in the same direction in both periods, and
Relays i and j are both sensitive in both periods
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Ijkh >Pj
Iikh >Pi

## Slide 4
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 3: Partial fault detection in relay j in period 1.
Type 3a: Relay j is stuck due to loss sensitivity in period 1 (case 3)
This happens when fault currents at relays i and j go in the same direction in both periods, and
Relays i and j are both sensitive in period 2.
Relay i is sensitive in period 2 and relay j is NOT sensitive at period 1.
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’pkh
I’jkh >Pj
I’ikh >Pi
Ijkh <Pj
Iikh >Pi
No sensitivity

## Slide 5
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 3: Partial fault detection in relay j in period 1.
Type 3b: Relay j is stuck due to current in the opposite direction in period 1 (case 4)
This happens when fault currents at relays i and j go in the opposite direction
in the first period, and Relays i and j are both sensitive in both periods.
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Ijkh >Pj
Iikh >Pi
Current in
the opposite
direction

## Slide 6
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 3: Partial fault detection in relay j in period 1.
Type 3c: Relay j is stuck due to current in the opposite direction and
no sensitivity in period 1 (case 5)
This happens when fault currents at relays i and j go in the opposite direction
in the first period, relay j is sensitive in the first period but no sensitive at second one,
and relay i is sensitive in both periods.
.
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Iikh >Pi
No sensitivity &
Current in
the opposite direction
Ijkh >Pj

## Slide 7
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 4: Partial fault detection in relay i: Relay i is stuck due to no sensitivity in period 1 (case 6)
This happens when fault currents at relays i and j go in the same direction in both periods, and
Relays i and j are both sensitive in period 2.
Relay i is sensitive in period 2 and relay j is NOT sensitive at period 1.
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Ijkh <Pj
Iikh <Pi
No sensitivity

## Slide 8
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 5: Partial fault detection in relay i and relay j:
Type 5a: Relay i and j are stuck due to no sensitivity in period 1 (case 7)
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’pkh
I’jkh >Pj
I’ikh >Pi
Ijkh <Pj
No sensitivity
Iikh <Pi
No sensitivity

## Slide 9
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 5: Partial fault detection in relay i and relay j:
Type 5b: Relay i is stuck due to no sensitivity and relay j is stuck due to current in
the opposite direction in period 1 (case 8)
This happens when fault currents at relays i and j go in the opposite direction in the first period,
relay i is not sensitive at first period and, relay j is sensitive in both periods .
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Ijkh >Pj
Current in
the opposite
direction
Iikh <Pi
No sensitivity

## Slide 10
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 5: Partial fault detection in relay i and relay j:
Type 5c: Relay i and j are stuck due to no sensitivity and relay j is stuck due to current
in the opposite direction in period 1 (case 9)
This happens when fault currents at relays i and j go in the opposite
direction in the first period, and relays i and j are not sensitive in the first period.
Relays i and j are sensitive at second period.
.
Ijkh ∢ qjkh
Iikh ∢ qikh
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh >Pj
I’ikh >Pi
Iikh <Pi
No sensitivity
No sensitivity &
Current in
the opposite direction
Ijkh >Pj

## Slide 11
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6a: Relay p is stuck due to current in the opposite direction in period 1 (case 10)
This happens when fault currents at q and p go in the opposite direction at first period, and
p is sensitive at first period
Iqkh ∢ qqkh
Ipkh ∢ qpkh
Current in
the opposite
direction
Ipkh >Pp

## Slide 12
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6b: Relay j is stuck due to current in the opposite direction in period 2 (case 11)
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
Current
in the opposite
direction

## Slide 13
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6c: Relay p is stuck due to no sensitivity in period 1 (case 12)
This happens when fault currents at q and p go in the same direction at first period, and
relay p is not sensitive at first period
Iqkh ∢ qqkh
Ipkh ∢ qpkh
no sensitivity
Ipkh <Pp

## Slide 14
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6d: Relay p is stuck due to current in the opposite direction and
no sensitivity in period 1 (case 13)
This happens when fault currents at q and p go in the same direction at first period, and
relay p is not sensitive at first period
Iqkh ∢ qqkh
Ipkh ∢ qpkh
no sensitivity
current in the
opposite direction
Ipkh <Pp

## Slide 15
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6e: Relay i is stuck due to current in the opposite direction in period 2 (case 14)
This happens when relay j is not sensitive in period 2 and currents go in the same direction
in period 2
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh ∢ q’qkh
I’ikh ∢ q’ikh
I’jkh <Pj
no
sensitivity

## Slide 16
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Case 14:
Type 6f: Abnormal operation of relay pair i-j.
This happens when relay i is not sensitive in period 2
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’ikh <Pj
no
sensitivity

## Slide 17
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
TB < TA
First Period (static) : t [0, Tqkh]
Line k Fault h
Type 6: No fault detection at all
Type 6f: Relay j is stuck due to no sensitivity in period 2 (case 15)
This happens when relay j is not sensitive in period 2
i
Backup Relay C
Backup
Relay D
Primary
Relay A
Primary
Relay B
q
j
p
Line k Fault h
*
Second Period (transient): t [Tqkh, Tikh or Tjkh]
*
I’jkh <Pj
no
sensitivity